Part-turn actuator with variable speed for modulating duty type SGMR with integral controls and fieldbus communication Profibus DP

Version according to wiring diagram TPC BA000-2A7-0520 TPA 50R200-0A0-000:

- Part-turn actuator for 90° valves with integral controls for type of duty S4-40 %

- Self-locking drive system with operating time adjustable in steps

- Electronically controlled motor in insulation class F, with thermistor motor protection

- Supply voltage 115/230 V, 50/60 Hz 1~ AC, connection via industrial plug

- Torque sensing over the whole travel, tripping value adjustable in steps

- Electronic end position detection and mechanical travel limitation

- Adjustable type of seating, limit or torque seating

- End positions adjustable via local controls without requiring any tools

- Continuous mechanical position indication

- Handwheel does not rotate during motor operation, without switch-over mechanism for manual operation

- Valve attachment according to ISO 5211, without spigot

- Integral controls in actuator

- Local controls with push buttons and indication lights

- Motor control via integral, contact-free power electronics

- Input and output signals via Profibus DP

- Integral positioner with setpoint and actual value via Profibus DP

- Permissible ambient temperature –25 °C to +70 °C, enclosure protection IP 68, corrosion protection KS (suitable for atmosphere with low pollutant concentration)

- Constant stall torque over the whole travel

- Overload protection in case of a 1.5 times higher max. torque in motor operation and manual operation

- Electrical connectors: 1 x Canon (power), 2 x Canon (fieldbus)

Options

- External supply of the control via 24 V DC

- Separately installed local controls

- Swing angles different to standard

- Flange with 8 bore solution

- Electrical connectors: 1 x Canon (power), 2 x Phoenix Contact (fieldbus)
TPC BA000-2A7-0540 TPA 50R200-0A0-000

Further options on request